|  |
| --- |
| Logo, company name  Description automatically generated |
|  |
|

|  |
| --- |
| C&S Fire-Safe Services, LLC Sent You a Quote  |
|  |
| C&S Fire-Safe Services, LLC submitted a quote for **Glendale Sr High School** for your review and approval. [Click here to view details, approve, or request changes to the quote](https://app.servicetrade.com/quoteview/view?id=b4jZ50s2ozBmJuRADu8rD2pxdpldCYD2fpOc%2Fu3YKRLhHje7KsKJ9VxwFrWQZZYj6nalqbmauJ3RPf9IEEsJ5BRfJdHQUr%2FPkDLJmy8LW4PSoaelaFkqeOKl13E%3D).  |
|  |
| We are pleased to submit the following quote for your consideration. The details of the scope of work, the hazards to be protected, and pricing are as follows:Scope of work:For the price listed below, C & S Fire-Safe Services LLC will:First Trip:* Measure 4 dry sprinklers.
* Order 4 dry sprinklers for replacement for ul testing.

Second Trip:* Put Fire system on test.
* Drain down dry system.
* Pull 4 dry sprinklers for UL testing.
* Install 4 new dry sprinklers.
* Our alarm tech will unwire the old tamper switch and the old pressure switch.
* Remove old dry valve and old os&y valve.
* Cut out patched 2 1/2” piece of pipe off the dry system. Install 4 feet of 2 1/2 pipe.
* Install amd-1 air maintence device.
* Install new dpv-1 dry valve and butterfly control valve.
* Re pipe FDC line from new valve to old fdc check valve.
* Our alarm tech will wire up the new pressure switch the new low air switch and the new butterfly valve plus make sure they are all functioning as designed.
* Fill wet system back up.
* Take Fire System off test.

If you schedule an appointment for our technician to complete the work and the facility is not ready upon his arrival the appropriate travel time will be charged and be invoiced to return and complete the work.Exceptions: Not included in quote.Painting or patch work.Electrical wiring costs are not included in this proposal.Specialty Equipment that may be needed (lifts etc).Permits are not included in this proposal ( if necessary).**Terms: We will require a 50% down payment of ( $ 6,642.84 ) No Parts can be ordered until we have the 50% down payment cleared.** **The dry sprinklers could take 4 weeks or more to come in after being ordered. The dry valve is currently in stock at the moment but depending on how long it takes to get approval and the money down it could be out of stock at time of order. Time line will be dependent upon stock on hand at time of order placement. No work can be scheduled until we have the parts in hand. We will call you as soon as they show up after ordering.**Payment Terms: Balance due upon completion and inspection of installation. |
|  |
| Quote: Quote for Inspection Repair at Glendale Sr High School Valid Until: 2/10/2023 Prepared By: Jason Valentino Address: 10598 Azalea-Glen Road, Glendale, OR 97442  |
|  |
| [View and Respond to Quote](https://app.servicetrade.com/quoteview/view?id=b4jZ50s2ozBmJuRADu8rD2pxdpldCYD2fpOc%2Fu3YKRLhHje7KsKJ9VxwFrWQZZYj6nalqbmauJ3RPf9IEEsJ5BRfJdHQUr%2FPkDLJmy8LW4PSoaelaFkqeOKl13E%3D)  |
|  |
| If you have any questions or concerns about this quote or you have received this email in error, please contact Jason Valentino at jason.v@csfiresafe.com or (541) 643-1184. Thank you!  |
|  |
|  |
|  |
| C&S Fire-Safe Services, LLC 541-673-1337 4019 Hooker Road Roseburg, OR 97470  |

 |